## Components-by-priority
Status: | 08/05/2017; 11:30 | CW19 |  | * for all device it must be enabled to pass through beam: vacuum functional and beam path free
Tunnel/ section | Components | Comp-name | Loop | Priority* | coor. person | Component test possible | Local Component test by/when | Parameters by/when | Cables by/when | Elec-HW by AE/when | Beckhoff fw by AE/when | Basic Karabo deployment by CAS/when | PLC side test by/when | End-to-End test | Comments
XTD2 | General vacuum |  |  | High | Dommach |  |  |  | VG/done |  | done
XTD2 | Absorder & V0 |  |  | High | Dommach |  |  |  | VG/done; WG19/wk9 |  | wk9 |  |  |  | Waiting for WG-19
XTD2 | Fast valve |  |  | High | Dommach |  |  |  | VG/done |  | done
XTD9-SPB | Fast valve |  |  | High | Dommach |  |  |  | VG/done |  | done
XTD9-FXE | Fast valve |  |  | High | Dommach |  |  |  | VG/done |  | done
XTD2 | Diff. pumping |  |  | High | Villanueva |  |  |  | VG/done |  | done
XTD2 | Diff. pumping |  |  | High | Villanueva |  |  |  | VG/done |  | done
XTD9 | General vacuum |  |  | High | Dommach |  |  |  | VG/done |  | done
XTD2 | Imager (SR) |  |  | High | Koch |  |  |  | 74/done |  | done
XTD2 | Imager (FEL) |  |  | High | Koch |  |  |  | 74/done |  | done
XTD2 | Imager |  |  | High | Koch |  |  |  | 74/done |  | done |  |  | started
XTD9 | Imager |  |  | High | Koch |  |  |  | 74/done |  | done
XTD9-SPB | Imager |  |  | High | Koch |  |  |  | 74/done |  | done
XTD9-FXE | Imager |  |  | High | Koch |  |  |  | 74/done |  | done
XTD2 | PSLIT |  |  | High | Sinn |  |  |  | done |  | done |  |  |  | LDVDT encoders: medium priority; MKK: water conection
XTD9-SPB | PBLM |  |  | High | Sinn |  |  |  | Elmo/wk9 |  | wk9
XTD9-FXE | PBLM |  |  | High | Sinn |  |  |  | Elmo/wk10 |  | wk9
XTD2 | XGM |  |  | High | Grünert |  |  |  | 74/done |  | done (?)
XTD2 | Solid attenuator |  |  | High | Sinn |  |  |  | done |  | done |  |  |  | Thermo-elements: medium priority
XTD2+9 | EPS system |  |  | High | Sinn |  |  |  | VG/wk8 |  | wk8
XTD2 | Mirror (1st) |  |  | High | Sinn |  |  |  | VG/done (C) |  | done |  |  |  | Piezo & sim. movement: low priority
XTD2 | Mirror (2nd) |  |  | High | Sinn |  |  |  | VG/done (C) |  | done |  |  |  | Piezo & sim. movement: low priority
XTD2 | Beam shutter |  |  | High | Dommach |  |  |  | VG/wk9
XTD9 | Mirror (Dist.) |  |  | High | Sinn |  |  |  | VG/done |  | done |  |  |  | Piezo & sim. movement: low priority
XTD9-SPB | Diff. pumping |  |  | Medium | Villanueva |  |  |  | done |  | wk8
XTD9-SPB | XGM |  |  | Medium | Grünert |  |  |  | vac Beck wk9 |  | wk9
XTD9-SPB | Diff. pumping |  |  | Medium | Villanueva |  |  |  | done |  | wk8
XTD9-SPB | FE/Beam shutter |  |  | High | Dommach |  |  |  | VG/wk9 (C) | [5 empty] | needs preparatory work by Wp-38
XTD9-FXE | FE/Beam shutter |  |  | High | Dommach |  |  |  | VG/wk9 (C) | [5 empty] | needs preparatory work by Wp-38
XHEXP-FXE | Vacuum system | FXE_OGT1_VAC | _loop1 | High | Galler | Patch panels installed CW12 | CW14-15 | CW14-15 | CW9 | CW9 | CW11-12 | CW12 | ???? |  | no vacuum tested so far | GREEN = TEST DONE
XHEXP-FXE | Motion | _OGT1_MOV | _loop1 | High | Galler |  | CW13 | CW13 | CW9 | CW9 | CW11-12 | CW12 | Cw20 |  | local test partially done, issues | YELLOW = MOTOR TESTED / ENCODER NOT TESTED/ISSUES FOUND
XHEXP-FXE | Beam Imaging U | _OGT1_BIU | _loop1 | High | Galler |  | CW13 | CW13 | CW9 | CW9 | CW11-12 | CW12 | CW13 |  |  | RED = NOT TESTED
XHEXP-FXE | Spectrum Ana. | _OGT1_SA | _loop1 | Low | Galler |  | ????? | ????? | CW9 | CW9 | CW11-12 | CW12 | CW13 |  | No patch panel availbale
XHEXP-FXE | PSLIT | _OGT1_PSLIT | _loop1 | High | Galler |  | CW13 | CW13 | CW9 | CW9 | CW11-12 | CW12 | CW13
XHEXP-FXE | Int. Pos. Monitor | _OGT1_IPM | _loop1 | Low | Galler |  | ????? | ????? | CW9 | CW9 | CW11-12 | CW12 | CW13 |  | no patch panels availba
XHEXP-FXE | Time Arr. Det. | _OGT1_TAD | _loop2 | Low | Galler |  | ????? | ????? | CW9 | CW9 | CW15, to fix firmware problem. Done | CW12 | CW13 |  | no patch panels availbale
XHEXP-FXE | Attenuator | _OGT1_ATT | _loop2 | High | Galler |  | CW13 | CW13 | CW9 | CW9 |  | CW12 | CW18
XHEXP-FXE | Vacuum system | _OGT2_VAC | _loop2 | High | Galler |  | CW19 | CW19 | CW9 | CW9 |  | CW12 | CW19 |  | Problem with Vacuum, feedback from AE necessary. All loops with VAC affected
XHEXP-FXE | Motion | _OGT2_MOV | _loop2 | High | Galler |  | CW13 | CW13 | CW9 | CW9 |  | CW12 | CW20 |  | no test done
XHEXP-FXE | Beam Imaging U | _OGT2_BIU-1 | _loop2 | High | Galler |  | CW13 | CW13 | CW9 | CW9 |  | CW12 | CW18
XHEXP-FXE | CRLs | _OGT2_CRL | _loop3 | High | Galler | Patch panels installed CW14 | CW20-21 | CW20-21 | CW9 | CW9 | CW16 | CW16 | CW20-21 |  | Wire problem
XHEXP-FXE | PSLIT | _OGT2_PSLIT | _loop3 | High | Galler |  | CW20 | CW20 | CW9 | CW9 | CW16 | CW16 | CW20 |  | Recent problems with encoders
XHEXP-FXE | Beam Imaging U | _OGT2_BIU-2 | _loop4 | High | Galler |  | CW19 | CW19 | CW9 | CW9 | CW17 | CW17 | CW19
XHEXP-FXE | Motion | _SMS_MOV | _loop4 | High | Galler |  | CW20-21 | CW20-21 | CW9 | CW9 | CW17 | CW17 | CW19
XHEXP-FXE | Clean-up slits | _AUXT_CSLIT | _loop4 | High | Galler |  | CW20-21 | CW20-21 | CW9 | CW9 | CW17 | CW17 | CW19
XHEXP-FXE | Motion | _DET_MOV | _loop4 | High | Galler |  | CW20-21 | CW20-21 | CW9 | CW9 | CW17 | CW17 | CW19
XHEXP-FXE | Johann Spectro. | _SMS_JSS | _loop5 | High | Galler |  | CW20-21 | CW20-21 | CW9 | CW9 | CW18 | CW18 | CW19
XHEXP-FXE | vHamos Spectro. | _SMS_VHS | _loop7 | High | Galler |  |  |  | CW9 | CW25 | CW25
XHEXP-FXE | Beam Imaging U | _OGT3_BIU | _loop8 | Low | Galler |  |  |  | CW9 | CW9 | CW20 |  |  |  | FXE request to have Infraestructure finished (air conditioning works) to go ahead with components installation. To be finished during this weekend. Ready CW20
XHEXP-FXE | Spectrum Ana. | _OGT3_SA | _loop8 | Low | Galler |  |  |  | CW9 | CW9 | CW20
XHEXP-FXE | Int. Pos. Monitor | _OGT3_IPM | _loop8 | Low | Galler |  |  |  | CW9 | CW9 | CW20
XHEXP-FXE | Motion | _OGT3_MOV | _loop8 | Low | Galler |  |  |  | CW9 | CW9 | CW20
XHEXP-FXE | User Table | _SMS_USR | _loop9 | Low | Galler |  |  |  | CW9 | CW9 | CW21
XHEXP-SPB-OPT | Vacuum system | SPB_MKB_VAC | SPB-01 | High | Bean | CW19 | done |  | Harting connections exchange to be fixed. Some connectors damage. CW20 | CW13 | CW20-21 |  |  |  | Once connector issues are fixed, finish BKF installation on CW20. If connectors issue takes longer, BKF installation will be done anyhow to permit to continue with PLC test.
XHEXP-SPB-OPT | Alignment laser | _MKB_ALAS | SPB-01 | High | Sato | CW19 | done |  |  | CW13 | CW20-21
XHEXP-SPB-OPT | PSLIT | _MKB_PSLIT | SPB-01 | High | Batchelor | CW19 | done |  |  | CW13 | CW20-21
XHEXP-SPB-OPT | Screen | _MKB_SCR‐1 | SPB-01 | High | Giewekemeyer | CW19 | done |  |  | CW19 | CW20-21
XHEXP-SPB-OPT | Micron Scale KB | _MKB_MHP | SPB-01 |  | Bean |  | only at FMB |  |  | CW19 | CW20-21
XHEXP-SPB-OPT | Micron Scale KB | _MKB_MHE | SPB-01 |  | Bean |  | only at FMB |  |  | CW19 | CW20-21
XHEXP-SPB-OPT | Screen | _MKB_SCR-2 | SPB-01 |  | Giewekemeyer | CW19 | done |  |  | CW13 | CW20-21
XHEXP-SPB-OPT | Micron Scale KB | _MKB_MVE | SPB-01 |  | Bean |  | only at FMB |  |  | CW19 | CW20-21
XHEXP-SPB-OPT | Micron Scale KB | _MKB_MVP | SPB-01 |  | Bean |  | only at FMB |  |  | CW19 | CW20-21
XHEXP-SPB-OPT | Vacuum system | _OHD_VAC | SPB-02 | High | Bean | CW20 | done |  |  | CW19 | CW20-21
XHEXP-SPB-OPT | Vacuum system | _TRN_VAC | SPB-02 | High | Bean | CW20 | done |  |  | CW19 | CW20-21
XHEXP-SPB-OPT | Clean-up slits | _OHD_CSLIT | SPB-02 | High | Stern | CW19 | done |  |  | CW13 | CW20-21
XHEXP-SPB-OPT | Screen | _OHD_SCR | SPB-02 | High | Giewekemeyer | CW19 | done |  |  | CW19 | CW20-21
XHEXP-SPB-OPT | Shutter | _OHD_SHUT | SPB-02 | High | Weinhausen |  |  |  | NO BECKHOFF
XHEXP-SPB-EXP | Alignment laser | _EHU_ALAS | SPB-03 | High | Sato |  |  |  |  | mod. 69
XHEXP-SPB-EXP | Screen | _EHU_SCR | SPB-03 | High | Giewekemeyer
XHEXP-SPB-EXP | Vacuum system | _EHU_VAC | SPB-03 | High | Bean |  |  |  |  | mod. 71
XHEXP-SPB-EXP | Attenuator | _EHU_ATT | SPB-03
XHEXP-SPB-EXP | Power Slit | _EHU_PSLIT | SPB-03
XHEXP-SPB-EXP | Clean-up slits | _NKB_CSLIT-1 | SPB-04 | High | Stern
XHEXP-SPB-EXP | Clean-up slits | _NKB_CSLIT-2 | SPB-04 | High | Stern
XHEXP-SPB-EXP | Screen | _NKB_SCR | SPB-04 | High | Giewekemeyer
XHEXP-SPB-EXP | Vacuum system | _NKB_VAC | SPB-04 | High | Bean
XHEXP-SPB-EXP | Nano Scale KB | _NKB_NHE | SPB-04 | [6 empty] | mod. 63
XHEXP-SPB-EXP | Nano Scale KB | _NKB_NVE | SPB-04 | [6 empty] | mod. 64 done
XHEXP-SPB-EXP | DPS | _IRU_DPA | ??? | High | Messerschmidt
XHEXP-SPB-EXP | IL Microscope | _IRU_INLINEMIC | ??? | High | Sikorski
XHEXP-SPB_EXP | Injector man. | _IRU_INJ-MOV | ??? | High | Sikorski
XHEXP-SPB-EXP | Fixed target mot | _IRU_FIXTARGET | ??? | High | Sikorski
XHEXP-SPB-EXP | Vacuum system | _IRU_VAC | SPB‐05 | High | Bean
XHEXP-SPB-EXP | AGIPD-z-move | _IRU_AGIPD1M… | ??? | High | Sikorski
XHEXP-SPB-EXP | L. detector chill | _IRU_CHL | SPB‐05 | High | Sikorski
XHEXP-SPB-EXP | AGIPD-controls | _IRU_AGIPD1M | SPB-06 | High | Sikorski
XHEXP-SPB-EXP | Comp Supp Struct | _EHC_CSS | SPB-07 | High | Bean
XHEXP-SPB-EXP | Vacuum system | _EHC_VAC | SPB-07 | High | Bean
XHEXP-SPB-EXP | Screen | _EHC_SCR-1 | SPB-07 | High | Giewekemeyer
XHEXP-SPB-EXP | Beam stop | _EHD_IBS | SPB-08 | High | Weinhausen
XHEXP | SASE1 PP laser |  |  | High | Lederer
XHEXP | SASE1 detector tests |  |  | High
XTD2 | K-Mono |  |  | Medium | Freund |  |  |  | 74/ |  | wk10
XTD2 | CRL |  |  | Medium | Batchelor | [5 empty] | wk11 |  |  |  | alignment expected in week 7 or 8
XTD2 | PBLM |  |  | Medium | Sinn |  |  |  | VG/ |  | wk9
XTD2 | MCP |  |  | Medium | Grünert |  |  |  | 74/ |  | wk10
XTD9 | Hirex (GU & CU) |  |  | Medium | Grünert |  |  |  | 74/ |  | wk12
XTD9 | PBLM |  |  | Medium | Sinn |  |  |  | VG/ |  | wk9
XTD9-SPB | CRL | _CRL | SPB Tunnel | High | Weinhausen | CW16 | CW16 |  | 84/wk6 |  | CW15 | CW15 | CW19 |  | - All motors commisssioned. Technosoft controller problem fixed and to be tested Friday 12th May by AE. Extend firmware to MCP. - Problems with encoders fixed, all are working. - Recent problem with a camera, AE will work on that beginnning CW20.
XTD9-FXE | Mono (2 chambers) |  |  | Medium | Sinn | CW16 | CW16 |  | VG/ |  | CW15 | CW15 | CW19
XTD9-SPB | Pulse picker | _PPU | SPB Tunnel | High | Weinhausen | CW16 | CW16 |  | 84/ |  | CW15 | CW15 | CW19
XTD9-SPB | Attenuator | _ATT | SPB Tunnel | High | Weinhausen | CW16 | CW16 |  | 84/wk6 |  | CW15 | CW15 | CW19
XTD9-SPB | Diagnostic Screen | _SCR | SPB Tunnel | High | Weinhausen | CW16 | CW16 |  |  |  | CW15 | CW15 | CW19